## config
Parameter | Value | Process Unit
model_path | models\clarifier\clarifier.joblib | clarifier
model_path | models\cstr\cstr.joblib | cstr

## decision_var
I_variables | Process Unit
flow_rate | clarifier, cstr
Q_was | clarifier
Q_ext | clarifier
O3_split_internal | clarifier
C1_surface_area | clarifier
C1_height | clarifier
KLa | cstr
V | cstr

## decision_var_bound
Variable | LowerBound | UpperBound | Process Unit
flow_rate | 10000 | 18446 | clarifier, cstr
Q_was | 100 | 450 | clarifier
Q_ext | 10000 | 25000 | clarifier
O3_split_internal | 0.1 | 0.7 | clarifier
C1_surface_area | 800 | 1800 | clarifier
C1_height | 2 | 6 | clarifier
KLa | 0 | 300 | cstr
V | 800 | 1500 | cstr

## fuzzy_goal
Goal | Target | Max | Source of Standard | Notes
Target_Effluent_COD (mg/L) | 60 | 300 | Philippines: DENR Administrative Order 2016-08[1] | Limits vary depending on the classification of the receiving water body (Class A, B, C, D for freshwater and SA, SB, SC, SD for marine water).[1][2] For establishments with influent BOD ≥ 3,000 mg/L discharging to specific water classes, different standards may apply.[1][3]
Target_Effluent_BOD (mg/L) | 30 | 100 | Philippines: DENR Administrative Order 2016-08[1] | Limits vary based on the classification of the receiving water body. For establishments with influent BOD ≥ 3,000 mg/L, specific effluent standards for BOD are enforced.[3][4]
Target_Effluent_TP (mg/L) | 1 | 10 | Philippines: DENR Administrative Order 2021-19[9][10] | The standard is for Phosphate as P and the limit varies depending on the classification of the receiving water body.[9][10]
Target_Effluent_TSS (mg/L) | 70 | 200 | Philippines: DENR Administrative Order 2016-08[1] | Limits are dependent on the classification of the receiving water body.
Target_Effluent_S_NH4 (mg/L) | 2 | 9 | Philippines: DENR Administrative Order 2021-19 | The limits for Ammonia as NH₃-N were updated in DAO 2021-19 and vary depending on the water body classification. For Class AA (freshwater) and SA (marine water), the standard is No Discharge Allowed (NDA).[3][4]
Target_Effluent_S_NO3 (mg/L) | 14 | 30 | Philippines: DENR Administrative Order 2016-08 | The limits vary depending on the classification of the receiving water body.[5][6]
CAPEX | 1000000 | 1700000 | n/a | n/a
AOC | 100000 | 180000 | n/a | n/a

## cost_var_cstr
Variable | Description | Value
V | Volume of the aerobic CSTR reactor [m³] | 2500
KLa | Required volumetric mass transfer coefficient [d⁻¹] | 60
DO_setpoint | Desired Dissolved Oxygen concentration in the reactor [g/m³ or mg/L] | 2
T | Operating temperature of the wastewater [°C] | 20
alpha_factor | Correction factor for oxygen transfer in wastewater vs clean water [-] | 0.85
beta_factor | Correction factor for oxygen saturation in wastewater vs clean water [-] | 0.95
C_s_20 | Saturation concentration of oxygen in clean water at 20°C, 1 atm [g/m³] | 9.09
tank_H_to_D_ratio | Target ratio of height to diameter for the cylindrical tank [-] | 0.5
tank_freeboard | Additional height of the tank wall above the water level [m] | 0.5
concrete_volume_factor | Factor to estimate concrete volume from tank structural volume [-] | 1.15
blower_pressure_head | Pressure required from the blower to overcome hydrostatic pressure and losses [Pa] | 60000
blower_efficiency | Overall efficiency of the blower and motor combination [-] | 0.75
SOTE | Standard Oxygen Transfer Efficiency of the selected diffusers [-] | 0.3
diffuser_density | Number of diffuser units required per square meter of tank floor [units/m²] | 1
mixing_energy_density | Power input required for complete mixing [W/m³] | 10
air_density_kg_m3 | Density of air at standard conditions [ kg/m ³] | 1.225
air_O2_percent_mass | Mass percentage of oxygen in air [-] | 0.232
unit_cost_concrete | All-in cost for reinforced concrete, including labor and formwork [USD/m³] | 600
unit_cost_excavation | Cost of excavation per cubic meter [USD/m³] | 50
unit_cost_blower | Cost per kilowatt of blower power [USD/kW] | 1200
unit_cost_diffuser | Cost per diffuser unit [USD/unit] | 150
unit_cost_mixer | Cost per kilowatt of mixer power [USD/kW] | 2000
factor_cost_piping | Piping & valve costs as a fraction of total equipment cost [-] | 0.25
factor_cost_instr | Instrumentation & control costs as a fraction of total equipment cost [-] | 0.15
factor_contingency | Contingency as a fraction of the subtotal CAPEX [-] | 0.15
electricity_price | Cost of electricity [USD/kWh] | 0.12
operating_hours | Annual operating hours [h/year] | 8760
factor_maint_equip | Annual maintenance for equipment as a fraction of equipment cost [-] | 0.05
factor_maint_civil | Annual maintenance for civil works as a fraction of civil cost [-] | 0.01

## capex_calc_cstr
Output Variable | Description | Calculation
C_s_T | Oxygen saturation concentration at operating temperature T [g/m³] | C_s_20 * (0.9777** (T - 20)) | --- Civil Works --- | --- Calculations for Tank Construction ---
tank_diameter | Calculated diameter of the cylindrical reactor [m] | ((4 * V) / (3.14159 * tank_H_to_D_ratio))**(1/3)
tank_water_depth | Calculated water depth in the reactor [m] | tank_diameter * tank_H_to_D_ratio
tank_total_height | Total height of the reactor including freeboard [m] | tank_water_depth + tank_freeboard
tank_excavation_vol | Volume of excavation required for the tank [m³] | (3.14159 / 4) * (tank_diameter**2) * tank_total_height
tank_floor_area | Floor area of the reactor tank [m²] | (3.14159 / 4) * (tank_diameter**2)
tank_wall_area | Surface area of the tank's cylindrical wall [m²] | 3.14159 * tank_diameter * tank_total_height
tank_structural_vol | Structural volume of concrete (floor + walls) assuming 0.3m thickness [m³] | (tank_floor_area * 0.3) + (tank_wall_area * 0.3)
tank_concrete_vol | Estimated total volume of concrete needed for the tank [m³] | tank_structural_vol * concrete_volume_factor
cost_civil | Total cost for tank excavation and construction [USD] | (tank_excavation_vol * unit_cost_excavation) + (tank_concrete_vol * unit_cost_concrete)
AOR_kg_d | Actual Oxygen Requirement for the process [kg O₂/d] | KLa * (beta_factor * C_s_T - DO_setpoint) * V / 1000 | --- Equipment Sizing & Costing --- | --- Calculations for Mechanical Equipment ---
SOTR_kg_d | Standard Oxygen Transfer Rate required [kg O₂/d] | AOR_kg_d / (alpha_factor * ((beta_factor * C_s_T - DO_setpoint) / C_s_20) * (1.024**(T - 20)))
required_airflow_m3_s | Required airflow from blowers at standard conditions [m³/s] | (SOTR_kg_d / (24 * 3600)) / (SOTE * air_density_kg_m3 * air_O2_percent_mass)
blower_power_kW | Required electrical power for the blowers [kW] | (required_airflow_m3_s * blower_pressure_head) / (blower_efficiency * 1000)
cost_blower | Capital cost of the blower system [USD] | blower_power_kW * unit_cost_blower
num_diffusers | Total number of diffusers required | tank_floor_area * diffuser_density
cost_diffusers | Capital cost of the diffuser system [USD] | num_diffusers * unit_cost_diffuser
mixer_power_kW | Required electrical power for the mixers [kW] | (V * mixing_energy_density) / 1000
cost_mixers | Capital cost of the mixing system [USD] | mixer_power_kW * unit_cost_mixer
cost_equipment_total | Total cost of all mechanical equipment [USD] | cost_blower + cost_diffusers + cost_mixers
cost_piping | Estimated capital cost for air piping and valves [USD] | cost_equipment_total * factor_cost_piping | --- CAPEX Calculation --- | --- Summation of All Capital Costs ---
cost_instrumentation | Estimated capital cost for I&C system [USD] | cost_equipment_total * factor_cost_instr
subtotal_capex | Total direct and indirect cost before contingency [USD] | cost_civil + cost_equipment_total + cost_piping + cost_instrumentation
cost_contingency | Contingency cost allowance [USD] | subtotal_capex * factor_contingency
CAPEX | Final Estimated Total Capital Expenditure [USD] | subtotal_capex + cost_contingency
annual_energy_cost | Annual cost of electricity for blowers and mixers [USD/year] | (blower_power_kW + mixer_power_kW) * operating_hours * electricity_price | --- AOC Calculation --- | --- Summation of All Annual Operating Costs ---
annual_maint_cost | Annual cost of maintenance for all assets [USD/year] | (cost_equipment_total * factor_maint_equip) + (cost_civil * factor_maint_civil)
AOC | Final Estimated Annual Operating Cost [USD/year] | annual_energy_cost + annual_maint_cost

## cost_var_clarifier
Variable | Description | Value
Q_was | Sludge wastage flowrate [m³/d] | 150
Q_ext | External recycle flowrate from C1 to A1 [m³/d] | 4500
C1_surface_area | Clarifier surface area [m²] | 1000
C1_height | Clarifier side water depth [m] | 4.5
unit_cost_concrete | All-in cost for reinforced concrete [USD/m³] | 650
unit_cost_excavation | Cost of excavation per cubic meter [USD/m³] | 55
unit_cost_scraper | Cost of scraper mechanism per square meter of clarifier area [USD/m²] | 250
unit_cost_pump | Cost per kilowatt of installed pump power [USD/kW] | 1100
unit_cost_electricity | Blended cost of electricity [USD/kWh] | 0.12
pump_head | Total dynamic head for RAS and WAS pumps [m] | 8
pump_efficiency | Overall efficiency of the pump and motor system [-] | 0.7
scraper_power_density | Power required for the scraper drive per unit area [kW/m²] | 0.0015
g | Acceleration due to gravity [m/s²] | 9.81
water_density | Density of water [ kg/m ³] | 1000
annual_op_days | Number of operating days per year [d] | 365
factor_civil_contingency | Contingency as a fraction of civil works cost [-] | 0.2
factor_mech_contingency | Contingency as a fraction of mechanical equipment cost [-] | 0.15
factor_eng_design | Engineering and design costs as a fraction of subtotal CAPEX [-] | 0.12
aoc_maintenance_factor | Annual maintenance cost as a fraction of equipment CAPEX [-] | 0.05
annual_labor_hours | Annual labor hours for operation and monitoring [hr/year] | 500
labor_rate | Blended hourly rate for operational labor [USD/hr] | 45

## capex_calc_clarifier
Output Variable | Description | Calculation
C1_diameter | Diameter of the circular clarifier [m] | (4 * C1_surface_area / 3.14159)**0.5 | --- Civil Works Sizing & Costing --- | --- Calculations for Clarifier Structure ---
C1_volume | Total volume of the clarifier [m³] | C1_surface_area * C1_height
cost_excavation | Cost for clarifier excavation [USD] | C1_volume * unit_cost_excavation
cost_concrete | Cost for clarifier concrete structure [USD] | C1_volume * unit_cost_concrete
cost_civil_subtotal | Subtotal cost for civil works [USD] | cost_excavation + cost_concrete
cost_civil_total | Total civil works cost with contingency [USD] | cost_civil_subtotal * (1 + factor_civil_contingency)
cost_scraper_equip | Capital cost of the scraper mechanism [USD] | C1_surface_area * unit_cost_scraper | --- Mechanical Equipment Sizing & Costing --- | --- Calculations for Scrapers and Pumps ---
pump_power_kW_ext | Required power for the external recycle (RAS) pump [kW] | (Q_ext / (24 * 3600)) * water_density * g * pump_head / (pump_efficiency * 1000)
pump_power_kW_was | Required power for the sludge wastage (WAS) pump [kW] | (Q_was / (24 * 3600)) * water_density * g * pump_head / (pump_efficiency * 1000)
pump_power_total_kW | Total installed pump power [kW] | pump_power_kW_ext + pump_power_kW_was
cost_pump_equip | Capital cost of all pumps [USD] | pump_power_total_kW * unit_cost_pump
cost_equipment_subtotal | Subtotal cost for mechanical equipment [USD] | cost_scraper_equip + cost_pump_equip
cost_equipment_total | Total mechanical equipment cost with contingency [USD] | cost_equipment_subtotal * (1 + factor_mech_contingency)
capex_subtotal | Subtotal project cost before engineering [USD] | cost_civil_total + cost_equipment_total | --- Total CAPEX Calculation --- | --- Summation of All Capital Costs ---
cost_engineering | Cost for engineering and design [USD] | capex_subtotal * factor_eng_design
CAPEX | Final Estimated Total Capital Expenditure [USD] | capex_subtotal + cost_engineering
scraper_power_kW | Operational power for the scraper drive [kW] | C1_surface_area * scraper_power_density | --- Annual Operating Cost (AOC) Calculation --- | --- Summation of All Annual Operating Costs ---
aoc_energy_pumping | Annual energy cost for pumping (RAS + WAS) [USD/year] | pump_power_total_kW * 24 * annual_op_days * unit_cost_electricity
aoc_energy_scraper | Annual energy cost for the scraper mechanism [USD/year] | scraper_power_kW * 24 * annual_op_days * unit_cost_electricity
aoc_energy_total | Total annual cost for energy [USD/year] | aoc_energy_pumping + aoc_energy_scraper
aoc_maintenance | Annual cost for maintenance [USD/year] | cost_equipment_total * aoc_maintenance_factor
aoc_labor | Annual cost for operational labor [USD/year] | annual_labor_hours * labor_rate
AOC | Final Estimated Total Annual Operating Cost [USD/year] | aoc_energy_total + aoc_maintenance + aoc_labor

## influent_compound_conc
Variable | Value
inf_S_I | 15.3018
inf_X_I | 1370.1019
inf_S_F | 1.4791
inf_S_A | 19.6603
inf_X_S | 300.1197
inf_S_NH4 | 43.5436
inf_S_N2 | 5.9128
inf_S_NO3 | 0.0053353
inf_S_PO4 | 17.247
inf_X_PP | 0.18005
inf_X_PHA | 87.3934
inf_X_H | 3022.1975
inf_X_AUT | 105.7547
inf_X_PAO | 80.0056
inf_S_ALK | 108.2037