## cost_var
Variable | Description | Value
# Design Inputs
C1_surface_area | Clarifier surface area [m2] | 750
C1_height | Clarifier height [m] | 4
C1_wall_thickness | Thickness of clarifier walls [m] | 0.4
C1_base_thickness | Thickness of clarifier base slab [m] | 0.5
Q_was | Sludge wastage flowrate [m3/d] | 100
Q_ext | External recycle flowrate from C1 to A1 [m3/d] | 5000
# Unit Costs (CAPEX)
unit_cost_concrete | Unit cost of concrete [USD/m3] | 500
unit_cost_steel | Unit cost of steel reinforcement [USD/ton] | 900
steel_reinforcement_ratio | Ratio of steel to concrete [ton/m3] | 0.1
equipment_cost_factor | Equipment cost as a fraction of construction cost | 0.6
engineering_cost_factor | Engineering & design as a fraction of construction + equipment cost | 0.15
contingency_factor | Contingency as a fraction of construction + equipment cost | 0.1
# Unit Costs & Factors (AOC)
scraper_motor_power | Power rating of the scraper motor [kW] | 3
sludge_pump_power | Power rating of the sludge pumps [kW] | 11
pump_efficiency | Overall efficiency of the sludge pumps | 0.75
TDH_pump | Total Dynamic Head for sludge pumps [m] | 10
electricity_price | Unit price of electricity [USD/kWh] | 0.12
maintenance_factor | Annual maintenance cost as a fraction of equipment cost | 0.03
labor_rate | Hourly labor rate for operators [USD/hour] | 45
daily_labor_hours | Daily operator hours for clarifier tasks [hours/day] | 1.5
# Constants
g | Gravitational acceleration [m/s2] | 9.81
rho | Density of water [kg/m3] | 1000

## capex_calc
Output Variable | Description | Calculation
# CAPEX Calculations
V_concrete_walls | Volume of concrete for walls (assumes square base) [m3] | (C1_surface_area**0.5 * 4) * C1_height * C1_wall_thickness
V_concrete_base | Volume of concrete for base [m3] | C1_surface_area * C1_base_thickness
V_concrete_total | Total volume of concrete [m3] | V_concrete_walls + V_concrete_base
W_steel | Total weight of steel reinforcement [ton] | V_concrete_total * steel_reinforcement_ratio
C_const | Total Construction Cost [USD] | (V_concrete_total * unit_cost_concrete) + (W_steel * unit_cost_steel)
C_equip | Total Equipment Cost [USD] | C_const * equipment_cost_factor
C_direct | Direct Costs (Construction + Equipment) [USD] | C_const + C_equip
C_engineering | Engineering & Design Cost [USD] | C_direct * engineering_cost_factor
C_contingency | Contingency Cost [USD] | C_direct * contingency_factor
CAPEX_C1 | **Total Clarifier CAPEX [USD]** | C_direct + C_engineering + C_contingency
# AOC Calculations
energy_scraper_yearly | Annual energy for scraper [kWh/year] | scraper_motor_power * 24 * 365
energy_pumps_yearly | Annual energy for sludge pumps [kWh/year] | ((Q_was + Q_ext) * rho * g * TDH_pump / pump_efficiency * 365) / (3600 * 1000)
C_energy | Annual Energy Cost [USD/year] | (energy_scraper_yearly + energy_pumps_yearly) * electricity_price
C_maint | Annual Maintenance Cost [USD/year] | C_equip * maintenance_factor
C_labor | Annual Labor Cost [USD/year] | daily_labor_hours * 365 * labor_rate
AOC_C1 | **Total Clarifier AOC [USD/year]** | C_energy + C_maint + C_labor